SAFETY

# Compressed gas cylinder storage inspection checklist

A walk of each cylinder store: cylinders upright and secured, caps on, labels legible, oxygen kept apart from fuel gases, and the area dry, ventilated and away from heat.

How often: Weekly   ·   Who: Area owner   ·   About 5 min   ·   12 items

| Site or area |  | Date and time |  |
| --- | --- | --- | --- |
| Asset or line |  | Completed by |  |

Before you use it

- OSHA 29 CFR 1910.101(a) requires employers to determine, by visual inspection, that the compressed gas cylinders under their control are in a safe condition.

- Under 1910.253(b)(4)(iii), oxygen cylinders in storage are kept at least 20 feet from fuel-gas cylinders and combustible materials such as oil or grease, or separated by a noncombustible barrier at least 5 feet high with a fire-resistance rating of at least half an hour.

- Inside buildings, cylinders are stored in a well-protected, well-ventilated, dry place, away from radiators and other sources of heat (1910.253(b)(2)).

## Store

| NO. | ITEM | RESULT | NOTES |
| --- | --- | --- | --- |
| 1 | Scan the store’s tag | Visited |  |
| 2 | Dry, ventilated and away from heat sources | Pass Fail N/A |  |
| 3 | No-smoking and hazard signs in place | Pass Fail N/A |  |

## Cylinders

| NO. | ITEM | RESULT | NOTES |
| --- | --- | --- | --- |
| 4 | Upright and secured against falling | Pass Fail N/A |  |
| 5 | Valve protection caps on cylinders not in use | Pass Fail N/A |  |
| 6 | Contents labels legible; no unlabeled cylinders | Pass Fail N/A |  |
| 7 | Full and empty cylinders kept apart and marked | Pass Fail N/A |  |
| 8 | No dents, bulges, deep corrosion or fire damage | Pass Fail N/A |  |
| 9 | Oxygen 20 feet from fuel gases and combustibles, or behind a 5-foot, half-hour fire barrier | Pass Fail N/A |  |

## Result

| NO. | ITEM | RESULT | NOTES |
| --- | --- | --- | --- |
| 10 | Photo of any problem | Photo taken |  |
| 11 | Notes |  |  |
| 12 | Checked by | Name ______________________________ Signature ______________________________ Date ______________________________ |  |

## Follow-up

For each failed check or reading out of limit: what was found, what was done, and the work order raised for it.

| NO. | WHAT WAS FOUND | ACTION OR WORK ORDER | OWNER | DUE |
| --- | --- | --- | --- | --- |

## References

- OSHA 29 CFR 1910.101, compressed gases

- OSHA 29 CFR 1910.253, oxygen-fuel gas welding and cutting

Free to use and adapt. To run it on mobile, with checkpoint scans, readings checked against their limits as they are entered, and photos and signatures attached to the check, see vardian.io/templates/compressed-gas-cylinder-inspection.