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SAFETY
Compressed gas cylinder storage inspection checklist
A walk of each cylinder store: cylinders upright and secured, caps on, labels legible, oxygen kept apart from fuel gases, and the area dry, ventilated and away from heat.
How often: Weekly   ·   Who: Area owner   ·   About 5 min   ·   12 items
	Site or area
	
	Date and time
	

	Asset or line
	
	Completed by
	


Before you use it
1. OSHA 29 CFR 1910.101(a) requires employers to determine, by visual inspection, that the compressed gas cylinders under their control are in a safe condition.
1. Under 1910.253(b)(4)(iii), oxygen cylinders in storage are kept at least 20 feet from fuel-gas cylinders and combustible materials such as oil or grease, or separated by a noncombustible barrier at least 5 feet high with a fire-resistance rating of at least half an hour.
1. Inside buildings, cylinders are stored in a well-protected, well-ventilated, dry place, away from radiators and other sources of heat (1910.253(b)(2)).
Store
	NO.
	ITEM
	RESULT
	NOTES

	1
	Scan the store’s tag
	 Visited
	

	2
	Dry, ventilated and away from heat sources
	 Pass     Fail     N/A
	

	3
	No-smoking and hazard signs in place
	 Pass     Fail     N/A
	


Cylinders
	NO.
	ITEM
	RESULT
	NOTES

	4
	Upright and secured against falling
	 Pass     Fail     N/A
	

	5
	Valve protection caps on cylinders not in use
	 Pass     Fail     N/A
	

	6
	Contents labels legible; no unlabeled cylinders
	 Pass     Fail     N/A
	

	7
	Full and empty cylinders kept apart and marked
	 Pass     Fail     N/A
	

	8
	No dents, bulges, deep corrosion or fire damage
	 Pass     Fail     N/A
	

	9
	Oxygen 20 feet from fuel gases and combustibles, or behind a 5-foot, half-hour fire barrier
	 Pass     Fail     N/A
	


Result
	NO.
	ITEM
	RESULT
	NOTES

	10
	Photo of any problem
	 Photo taken
	

	11
	Notes
	


	12
	Checked by
	Name  ______________________________
Signature  ______________________________
Date  ______________________________


Follow-up
For each failed check or reading out of limit: what was found, what was done, and the work order raised for it.
	NO.
	WHAT WAS FOUND
	ACTION OR WORK ORDER
	OWNER
	DUE

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	


References
1. OSHA 29 CFR 1910.101, compressed gases
1. OSHA 29 CFR 1910.253, oxygen-fuel gas welding and cutting
Free to use and adapt. To run it on mobile, with checkpoint scans, readings checked against their limits as they are entered, and photos and signatures attached to the check, see vardian.io/templates/compressed-gas-cylinder-inspection.
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