## Checklist
Hot work permit
The permit for welding, cutting and other hot work: the area inspected, combustibles within 35 feet removed or protected, a fire watch, and a final check after the work ends.
How often: Each job · Who: Permit issuer and fire watch · About 10 min · 14 items
| Site or area |  |  |  | Date and time
| Asset or line |  |  |  | Completed by
No. | Item | Type | Result | Unit | Low limit | High limit | Status | Notes
Job
1 | Scan the work location’s tag | Checkpoint scan
2 | Location and equipment | Note
3 | Work | Choice
4 | Permit valid from and to | Note
Precautions
5 | Area inspected by the person authorizing the work | Pass / fail
6 | Combustibles within 35 feet removed or covered with fire-resistant shields | Pass / fail
7 | Floor swept clean within 35 feet; combustible floors wet or covered | Pass / fail
8 | Wall and floor openings within 35 feet covered | Pass / fail
9 | Fire extinguisher at the work location | Pass / fail
Fire watch
10 | Fire watch assigned, with an extinguisher and trained to use it | Pass / fail
11 | Fire watch kept at least 30 minutes after the work ended | Pass / fail
12 | Time of the final check | Note
Sign-off
13 | Permit issuer | Signature
14 | Fire watch | Signature
Before you use it
• OSHA 29 CFR 1910.252(a)(2)(iv) requires the area to be inspected by the person responsible for authorizing welding and cutting, who designates the precautions, preferably in a written permit.
• A fire watch is required where more than a minor fire might develop, for example when appreciable combustibles are closer than 35 feet, and it stays for at least half an hour after the work ends (1910.252(a)(2)(iii)).
• Combustible material on the floor is swept clean for a 35-foot radius (1910.252(a)(2)(v)). Add your site’s and your insurer’s own hot work rules.
References
OSHA 29 CFR 1910.252, welding, cutting and brazing: general requirements
Free to use and adapt. To run it on mobile, with checkpoint scans, readings checked against their limits as they are entered, and photos and signatures attached to the check, see vardian.io/templates/hot-work-permit.
https://vardian.io/templates/hot-work-permit

## Follow-up
Follow-up: Hot work permit
For each failed check or reading out of limit: what was found, what was done, and the work order raised for it.
No. | What was found | Action or work order | Owner | Due | Closed

## Lists (hidden)
Visited | Welding | Pass | Yes
Not visited | Cutting | Fail | No
| Grinding | N/A
Brazing or soldering